## Table-A-Registers
No | Register | Register name | Meaning | High Byte | Low Byte
0 | 0x00 | REG TYPE REG | Device Model (see 0x33)
1 | 0x01 | REG VALUE REG | Gas Concentration Value (see 0x06)
2 | 0x02 | REG STATUS REG | Fault Status Code (see 0x19)
3 | 0x03 | REG MAX VALUE | Maximum Measurement Range (see 0x23)
4 | 0x04 | REG UNIT | Measurement Unit (see 0x22)
5 | 0x05 | DEVICE STATUS REG | Device Status | Sensor Operational Modes (see Table-B) | Sensor Fault Type (see Table-C)
6 | 0x06 | GAS CONCT VALUE REG | Gas Concentration Value | Gas Conct Value = register(0x06)/ register(0x29)
7 | 0x07 | GAS CONCT PERCENT REG | Gas Concentration Percent | Gas Conct. Percent
8 | 0x08 | L TWA VALUE REG | TWA Value -15 minute time weighted average value | Twa Value -15 minute time weighted average value
9 | 0x09 | S TWA VALUE REG | TWA Value - 1 minute time weighted average value | TwaValue - 1 minute time weighted average value
10 | 0x0A | READ ADC VALUE REG | ADC reading counter | Read Adc Value (counter)
11 | 0x0B | SENSOR TEMP REG | Sensor Temperature | Sensor Temp value
12 | 0x0C | IN VOL VALUE REG | Input Voltage | Input Voltage Value = read / 10
13 | 0x0D | CURRENT OUTPUT REG | Current Output (mA) | Current Output (mA) = read /100
14 | 0x0E | CUR LINE RESISTOR REG | Current Line Resistor | Current Line Resistor
15 | 0x0F | DATE YEAR MON REG | Year (last two digit) | Year (2022 for 22) | Month
16 | 0x10 | DATE DAY REG | Day |  | Day
17 | 0x11 | TIME HOUR MIN REG | Time- Hour and Minute | Hour | Minute
18 | 0x12 | TIME SEC REG | Time-Second |  | Second
19 | 0x13 | TEST STATUS REG | Self Test Register | Self Test Register
20 | 0x14 | Intenal Use only
21 | 0x15 | UNUSED REG | Span Set Time | Span Set Time = read / 2
22 | 0x16 | CALIBRATION TIME REG | Calibration Time | Calibration Time = read / 2
23 | 0x17 | SENSOR VOL VALUE REG | Sensor Voltage Level | Sensor Voltage Value (v) = read / 1000
24 | 0x18 | LAMP VOL VALUE REG | Lamp Voltage Level | Lamp Voltage Value (V)= read / 1000
25 | 0x19 | FAULT STATUS REG | Fault Status Code | Fault Status Code
26 | 0x1A | ALARM1 CONFIG REG | Alarm1 Off Delay | Alarm1 Off Delay | Alarm1 Auto Reset => 1.(bit 1-on 0-off) Alarm1 Relay => 2. bit (1-Enerjed 0-De-enerjed) Alarm1 Direction => 3.bit (1-İnen Kenar 0-Çıkan Kenar)
27 | 0x1B | ALARM2 CONFIG REG | Alarm2 Off Delay | Alarm2 Off Delay | Alarm2 Auto Reset => 1. bit Alarm2 Relay => 2. bit Alarm2 Direction => 3.bit
28 | 0x1C | ALARM3 CONFIG REG | Alarm3 Off Delay | Alarm3 Off Delay | Alarm3AutoReset => 0. bit Alarm3Relay => 1. bit Alarm3Direction => 2.bit
29 | 0x1D | ANALOG OUT LEV1 REG | Analog Out Level1 Fault State | Analog Out Level1 Fault State = read / 10 | Analog Out Level1 WarmUp = read / 10
30 | 0x1E | ANALOG OUT LEV2 REG | Analog Out Level2 calibration | Analog Out Level2 calibration = read / 10 | Analog Out Level2 inhibit = read / 10
31 | 0x1F | ANALOG OUT LEV3 REG | Analog Out Level3 Overrange State | Analog Out Level3 Overrange State = read / 10 | Analog Out Level3 Zero = read / 10
32 | 0x20 | SENSOR TYPE REG | Sensor Type | INFRARED SENSOR= 0x4576, EEC SENSOR= 0x8844, CATALYTIC SENSOR= 0x6522, SEMICONDUCTOR SENSOR= 0x1906, PID SENSOR = 0x3754
33 | 0x21 | GAS TYPE REG | Gas Type | Gas Type (see Table-D)
34 | 0x22 | MEASR UNIT REG | Measurement Unit (decimal) | Measurement Unit | PPM =2, VOL =3, LEL =4, PPB =5,
35 | 0x23 | GAS CONCT RANGE REG | Maximum Measurement Range | Maximum Measurement Range = > read / register (0x29-ScalingFactor)
36 | 0x24 | GAS LEL VALUE REG | Maximum Measurement Volume | Max Measr Volume = read / 10
37 | 0x25 | CAL GAS TYPE REG | Relative Sensitivity | Relative Sensitivity
38 | 0x26 | ALARM1 LEVEL REG | Alarm1 Level | Alarm1 Level = read / 0x29 register (ScalingFactor)
39 | 0x27 | ALARM2 LEVEL REG | Alarm2 Level | Alarm2 Level = read / 0x29 register (ScalingFactor)
40 | 0x28 | ALARM3 LEVEL REG | Alarm3 Level | Alarm3 Level = read / 0x29 register (ScalingFactor)
41 | 0x29 | SCALING FACTOR REG | Scaling Factor | Scaling Factor
42 | 0x2A | IR PEAK RD DELAY REG | Ir Peak Read Delay | Ir Peak Read Delay
43 | 0x2B | IR DEEP RD DELAY REG | Ir Deep Read Delay | Ir Deep Read Delay
44 | 0x2C | IR LAMP PERIOD REG | Ir Lamp Period | Ir Lamp Period
45 | 0x2D | FW VERSION 1 REG | Firmware level detail | read.xx.xx | xx.read.xx
46 | 0x2E | FW VERSION 2 REG | Firmware level detail |  | xx.xx.read
47 | 0x2F | FW DATE 1 REG | Firmware date (Year/Month) | FW DATE = Year | FW DATE => moon
48 | 0x30 | FW DATE 2 REG | Firmware date (Day) |  | FW DATE => day
49 | 0x31 | DISPLAY LANGUAGE | Display Language (decimal) |  | ENGLISH = 0, TURKISH = 1, RUSIIAN = 2, NO DSP LNG = 3,
50 | 0x32 | BAUD RATE REG | Communication Speed | BAUD RATE
51 | 0x33 | DET MODEL REG | Device Model | GENERIC MODEL DET= 0x5202, P MODEL DET= 0x5687, PQ MODEL DET= 0x5420, PPS MODEL DET= 0x5831, PE MODEL DET= 0x5810, PEM MODEL DET= 0x5893, PC3 MODEL DET= 0x5685, SOMA MODEL DET= 0x5324, PX MODEL= 0x4934, AN2 MODEL = 0x4731
52 | 0x34 | MAN ID NUMB1 2 REG | Manufacturing ID | ManId => 1. character Char(read) | ManId => 2. character Char(read)
53 | 0x35 | MAN ID NUMB3 4 REG | Manufacturing ID | ManId => 3. character Char(read) | ManId => 4. character Char(read)
54 | 0x36 | MAN ID NUMB5 6 REG | Manufacturing ID | ManId => 5. character Char(read) | ManId => 6. character Char(read)
55 | 0x37 | MAN ID NUMB7 8 REG | Manufacturing ID | ManId => 7. character Char( read) | ManId => 8. character Char(read)
56 | 0x38 | BASE SER NUMB1 2 REG | Base Seri No | Base Seri No => 1. character Char( read) | Base Seri No => 2. character Char(read)
57 | 0x39 | BASE SER NUMB3 4 REG | Base Seri No | Base Seri No => 3. character Char( read) | Base Seri No => 4. character Char(read)
58 | 0x3A | BASE SER NUMB5 6 REG | Base Seri No | Base Seri No => 5. character Char( read) | Base Seri No => 6. character Char(read)
59 | 0x3B | BASE SER NUMB7 8 REG | Base Seri No | Base Seri No => 7. character Char( read) | Base Seri No => 8. character Char(read)
60 | 0x3C | SERAIL NUMBER1 2 REG | Serial Number | Serial Number => 1. character Char( read) | Serial Number => 2. character Char(read)
61 | 0x3D | SERAIL NUMBER3 4 REG | Serial Number | Serial Number => 3. character Char( read) | Serial Number => 4. character Char(read)
62 | 0x3E | SERAIL NUMBER5 6 REG | Serial Number | Serial Number => 5. character Char( read) | Serial Number => 6. character Char(read)
63 | 0x3F | SERAIL NUMBER7 8 REG | Serial Number | Serial Number => 7. character Char( read) | Serial Number => 8. character Char(read)
64 | 0x40 | LOC STRNG STRT REG | Location Text | 64. register dan başlayarak Char(reg64H) + Char(reg64L) + Char(reg65H) + Char(reg65L) + … + Char(reg76H) + Char(reg76L)
76 | 0x4C | LOC STRNG END REG | Location Text
77 | 0x4D | BASE CONFIG REG | Base Configuration Details |  | Congfig Bump Test => 1. bit 1-on 0-off Congfig Zero => 2. bit RS485 FLT INHIBIT1 => 3 bit RELAY CARD FLT INHIBIT1 => 4. bit CALIBRASYON DUE => 5. bit BATTERY FAULT =6. bit
78 | 0x4E | TEST DATE YEAR MONTH | Test Date (Year/Month) | TEST DATE => year | TEST DATE => moon
79 | 0x4F | TEST DATE DATE CYCLE | Test Date (Day) | TEST DATE => day
80 | 0x50 | ZERO VAL REG | Zero Value | Zero Value
81 | 0x51 | SPAN VAL REG | Span Value | Span Value
82 | 0x52 | SPAN TEMP REG | Span Temperature | Span Temp =read / 10
83 | 0x53 | CALB CONC VAL REG | Calibration Gas Concentration Level | Calb Conc Value = > read / register (0x29 -ScalingFactor)
84 | 0x54 | CALB DATE YEAR MONTH | year | year | moon
85 | 0x55 | CALB DATE DATE | day | day
86 | 0x56 | CALB CYCLE REG | Cal. Cycle period moon | Cal. Cycle period moon
87 | 0x57 | SECOND SPAN VAL REG | Second Span Value | Second Span Value
88 | 0x58 | Intenal Use only
89 | 0x59 | Intenal Use only
90 | 0x5A | Intenal Use only
91 | 0x5B | Intenal Use only
92 | 0x5C | Intenal Use only
93 | 0x5D | Intenal Use only
94 | 0x5E | Intenal Use only
95 | 0x5F | Intenal Use only
96 | 0x60 | Intenal Use only
97 | 0x61 | Intenal Use only
98 | 0x62 | Intenal Use only
99 | 0x63 | Intenal Use only
100 | 0x64 | Intenal Use only
101 | 0x65 | Intenal Use only
102 | 0x66 | Intenal Use only
103 | 0x67 | Intenal Use only
104 | 0x68 | ALRM HYSTERESIS 1 2 REG | A1 Hysteresis | A1 Hysteresis | A2 Hysteresis
105 | 0x69 | ALRM HYSTERESIS 3 REG | A3 Hysteresis | A3 Hysteresis
106 | 0x6A | PID SEN GAS TYPE | PID Gas Index | PID register1 = read + 1
107 | 0x6B | SEN SUPPLY VOLTAGE | Sensor Voltage | Sensor Voltage (V)= read / 10
108 | 0x6D | Intenal Use only
109 | 0x6E | Intenal Use only
110 | 0x6F | Intenal Use only

## Table-B-Sensor Operation Modes
Sensor Operational Modes
Value | Meaning
0x00 | QUIESCENT
0x01 | ALARM
0x02 | WARM_UP
0x03 | FAULT
0x04 | INHIBIT
0x05 | FUNCTIONAL_TEST
0x06 | CALIBRATION
0x07 | SETUP

## Table-C-Sensor Fault Type
Detector Fault Type
Value | Code | Description
0x00 | NO FAULT | No Fault
0X0D | PROGRAM ERR | Firmware load error
0x10 | SENSOR ERROR | Sensor is in fault condition
0x11 | NOT CONNECTED | Sensor is not connected or one-wire communication doesnot work.
0x12 | SIGNAL OUT RANGE | Sensor signal is out of range
0x13 | TEMPERATURE ERR | Temperature is out of defined range
0x14 | SENSOR_TYPE ERR | Sensor type definiton read from sensor module does not match the recorded configuration value
0x15 | TIMER ERR | IR Sensor Timer error
0x16 | SENSOR REG ERR | Sensor power voltage error
0x17 | IR LAMP REG ERR | IR sensor lamp regulator is in fault condition and does not generate lamp feeding signal
0x18 | SENSOR SWITCHED OFF | Pellistor sensor power off due to overrange for sensor protection
0x19 | SENSOR REGULATOR | Sensor Regulator Voltage out of range
0x1A | SENSOR MODEL ERR | Sensor Model does not match with the settings
0x1B | SENSOR DATA CRC ERR | Sensor Data corruption detected
0x1C | NEGATIVE DRIFT | Sensor signal is below defined minimum value
0X1D | SENSOR NTC ERR | Sensor temperature reading failed
0x1E | OVERRANGE ERR | Sensor is in overrange status
0x20 | ADC ERR | ADC circuit is not functioning correctly
0x21 | INT ADC1 ERR | Internal ADC1 signal level is not correct
0X22 | INT ADC2 ERR | Internal ADC2 signal level is not correct
0X23 | EXT ADC ERR | External ADC signal level is not correct
0X24 | ADC REF ERR | ADC reference signal level is not correct
0x30 | CURRENT OUTPUT ERR | Detector is not generating analogue output signal
0x31 | DAC OUTPUT ERROR | MCU DAC output signal level is out of range
0x32 | LINE OUTPUT OPEN | Analogue current output not connected
0x33 | LINE OUPUT SHORT | Analogue current output short circuited
0x40 | SUPPLY VOL ERR | Power input failure
0x41 | LOW SUPPLY VOLTAGE err | Power input is below minimum level
0x42 | HIGH SUPPLY VOLTAGE | Power input is above maximum level
0x50 | PRG RAM ERROR | RAM fault detected
0x51 | RAM TEST FAILURE | RAM test is failed
0x52 | STACK OVERFLOW ERR | Stack overflow error
0x60 | PRG FLASH ERR | Flash error detected
0x61 | FLASH CRC ERR | Flash data corrupt
0x62 | CRC INIT ERR | CRC calculation error
0x63 | XTRM STNGS CRC ERR | Main board parameter corruption
0x64 | XTRM USER STNGS ERR | Main board user parameter corruption
0x70 | SENSOR EEPROM ERR | Sensor parameter corruption
0x71 | SETTINGS CRC ERR | Transmitter parameter corruption
0x72 | ONE WIRE ERR | Main board anad sensor board communication error
0x73 | TYPE CRC ERR | Sensor type could not read from sensor module
0x80 | DUE DATE ERROR | Defined test period is passed, test execution is needed
0x81 | SENSOR CALIB DUE | Defined calibration period is passed, calibration is needed
0x82 | BUMP TEST DUE | Defined bump test period is passed, bump test needed
0x90 | BATTERY ERROR | Battery is in fault condition
0x91 | BATTERY VOLTAGE LOW | Battery level is low
0x92 | NO BATTERY DETECTED | No battery is installed
0xA0 | DETECTOR BASE ERR | Transmitter board failure
0xA1 | DSP COMMM ERR | Display communication failure
0xA2 | RS485 COMMM ERR | RS485 communication failure
0xA3 | RS485 PORT ERR | RS485 communication port error
0xA4 | HART PORT ERR | HART communication port error
0xB0 | RELAY CARD ERR | Relay Module failure
0xB1 | FAULT RELAY ERR | Fault relay failure
0xB2 | ALARM1 RELAY ERR | Alarm-1 relay failure
0xB3 | ALARM2 RELAY ERR | Alarm-2 relay failure
0xB4 | FLT RELAY ERR | Fault relay failure
0xB5 | AL1 RELAY ERR | Alarm-1 relay failure
0xB6 | AL2 RELAY ERR | Alarm-2 relay failure
0XC0 | CPU ERR | CPU failure
0XC1 | CPU TEST FAILURE | CPU test failure
0XD1 | STACK TEST FAILURE | Stack test failure
0XD2 | STACK OVERFLOW ERR | Stack overflow error
0XD3 | FLOW CONTROL ERR | Software flowcontrol failure
0XE0 | AMBIENT ERROR | Ambient temperature is out of defined range
0XE1 | HIGH TEMP ERR | Temperature is higher than maximum allowed level
0xE2 | LOW TEMP ERR | Temperature is lower than minimum allowed level

## Table-D-Gas List
Gas Code List
Code | Formula | Gas
30 | LPG | LPG
31 | CH4 | Methane
32 | CNH2N2 | Petrol Vapour
33 | C4H10 | n-Butane
34 | C3H8 | Propane
35 | C6H14 | Hexane
36 | H2 | Hydrogen
37 | C5H12 | N-pentane
38 | C6H5CH3 | Toluene
39 | CH3OH | Methanol
40 | C7H16 | N-heptane
41 | C8H18 | Octane
42 | C2H5OH | Ethanol
43 | CH3_C2H4COOH | Iso-propanol
44 | CO | Carbon Monoxide
45 | C3H6O | Acetone
46 | C4H8O | Methyl ethyl ketone
47 | C2H5COOH | Ethyl acetate
48 | NH3 | Amonia
49 | C2H4 | Ethylene
50 | CH3COOH | Acetic acid
51 | C4H9COOH | Butyl acetate
52 | C6H12 | Cyclohexane
53 | C5H10 | Cyclopentane
54 | C4H8O2 | Dioxane
55 | C2H6 | Ethane
56 | C4H10O | Butyl Alcohol
57 | C8H8 | Stylene
58 | C3H6 | Propylene
59 | C8H10 | Xylene
60 | C2H2 | Acetylene
61 | C6H6 | Benzene
62 | C2H4O | Etylene Oxide
63 | C4H6O2 | Vinyl Acetate
64 | H2S | Hydrogen Sulfide
65 | O2 | Oxygen
66 | SO2 | Sulphur Dioxide
67 | NO | Nitric Oxide
68 | NO2 | Nitrogen Dioxide
69 | CL2 | Clorin
70 | HC | Hydrocarbon
71 | CO2 | Carbon Dioxide
72 | FREON | Refrigerant gases
73 | JP8 | Jet Fuel
74 | CH2O | Formaldehit
75 | HCN | Hydrocyanic Acid
76 | H2O2 | Hydrogen Peroxide
77 | C9H20 | Nonane
78 | C2H4O | Acetaldehyde
79 | HCl | Hydrogen Chloride
80 | TVOC | TVOC
81 | VOC | VOC
82 | O3 | Ozone
83 | HF | Hydrogen Floride
84 | PH3 | Phospine
85 | C4H8 | Isobutylene
86 | SiH4 | Silane
87 | B2H6 | Diborane
88 | AsH3 | Arsine
89 | GeH4 | Germane
90 | Air | Air Quality
91 | A2L | A2L Refrigerant Gas